### Performance based approach

|  | The performance based approach as opposed to prescriptive design involves the assessment of three basic components comprising the likely fire behaviour, heat transfer to the structure and the structural response. The overall complexity of the design depends on the assumptions and methods adopted to predict each of the three design components. |
| --- | --- |

In the following, the three design components are discussed.

- Fire Modelling

- Thermal Analysis

- Structural Analysis

### Fire Modelling

Figure 1 Options for fire modelling in compartments

| Fire model | Norminal fires | Time equivalences | Compartment fires | Zone Models | CFD / field models |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Parametric | Localised | One-zone | Two-zone |  |
| Complexity | Simple | Intermediate | Advanced |
| Fire Behaviour | Post-flashover fires | Pre-flashover fires | Post-flashover fires | Pre-flashover / localised fires | Complete temperature-time relationships |
| Temperature distribution | Uniform in whole compartment | Non-uniform along plume | Uniform | Uniform in each layer | Time and space dependent |
| Input parameters | Fire type No physical parameters | Fire load Ventilation conditions Thermal properties of boundary Compartment size | Fire load & size Height of ceiling | Fire load Ventilation conditions Thermal properties of boundary Compartment size Detailed input for heat & mass balance of the system | Detailed input for solving the fundamental equations of the fluid flow |
| Design tools | BSEN1991-1-2 | COMPF2 OZone SFIRE-4 | CCFM CFAST OZone | FDS SMARTFIRE SOFIE |
|  | PD7974-1 |  | PD7974-1 |  |  |  |  |
|  | Simple equations for hand calculations | Spreadsheet | Simple equations | Computer models |

Generally, the factors influencing the severity of a compartment fire can be summarised as follows:

- Fire load type, density and distribution

- Combustion behaviour of fire load

- Compartment size and geometry

- Ventilation conditions of compartment

- Thermal properties of compartment boundary

The occurrence of flashover in a compartment fire imposes a transition to the fire development. Therefore, many fire models are classified under pre- or post-flashover, except for the computational fluid dynamic (CFD) models, which cover both phases.

There are a number of options available to calculate the fire severity as follows:

- Standard/Nominal Fire Models – standard, external and hydrocarbon fires

- Time Equivalences – relate standard fires to real fires

- Parametric Fire Models – for post-flashover fires

- Localised fires – for pre-flashover fires

- External window fires – for fires through openings of fire compartment

- Zone Models – one-zone models for pre-flashover fires – two-zone models for post-flashover fires

- CFD or Field Models – for general fire and smoke modelling

The level of complexity increases from simple fire models to field models as shown in Figure 1. Basically, the first four fire models can be considered as simple models, whereas the zone and CFD models are advanced models. The input parameters for each of these models are quite different with the advanced models requiring very detailed input data and simple models requiring little input.

In the simple fire models, the gas temperature of a compartment is taken as uniform and represented by a temperature-time relationship. The smoke movement and fire spread cannot be considered. They are more suitable for modelling post-flashover fires.

The advanced fire models are normally theoretical computer models that simulate the heat and mass transfer process associated with a compartment fire. They can predict compartment gas temperatures in much more detail. The smoke movement and fire spread may be taken into account. As reflected in their names, a zone model may present the gas temperature into single or different zones, whereas a CFD model provides a space/field dependent gas temperatures distribution.

Each of the fire models will be discussed in the section.

### Fire Behaviour

PD7974-1 (2003) provides the basics of initiation and development of compartment fires. Basically, an enclosure fire may include some or all of the following phases of development, which are also illustrated in Figure 2.

Figure 2 Phases of development of the fire

| Incipient phase | Heating of potential fuel is taking place through a variety of combustion processes such as smouldering, flaming or radiant. |
| --- | --- |
| Growth phase (pre-flashover) | Ignition is the beginning of fire development. At the initial growth phase, the fire will be normally small and localized in a compartment. An accumulation of smoke and combustion products (pyrolysis) in a layer beneath the ceiling will gradually form a hotter upper layer in the compartment, with a relatively cooler and cleaner layer at the bottom. With sufficient supplies of fuel and oxygen and without the interruption of fire fighting, the fire will grow larger and release more hot gases and pyrolysis to the smoke layer. The smoke layer will descend as it becomes thicker. |
| Flashover | In case of fire developing into flashover, the radiation from the burning flame and the hot smoke layer may lead to an instant ignition of unburned combustible materials in the compartment. The whole compartment will be engulfed in fire and smoke. |
| Fully developed phase (post-flashover) | After the flashover, the fire enters a fully developed stage with the rate of heat release reaching the maximum and the burning rate remaining substantially steady. The fire may be ventilation or fuel controlled. Normally, this is the most critical stage that structural damage and fire spread may occur. |
| Decay phase | After a period of sustained burning, the rate of burning decreases as the combustible materials is consumed and the fire now enters the decay phase. |
| Extinction | The fire will eventually cease when all combustible materials have been consumed and there is no more energy being released. |

### Nominal Fires

The nominal or standard fire curves are the simplest way to represent a fire by pre-defining some arbitrary temperature-time relationships, which are independent on ventilation and boundary conditions. Historically, they were developed for fire resistance furnace tests of building materials and elements for their classification and verification. The main disadvantages and limitations of standard fires include:

- The standard fires do not represent real natural fire. The differences in the heating rate, fire intensity and duration between the standard and real fires can result in different structural behaviour. For example, a short duration high temperature fire can result in spalling of concrete exposing steel reinforcement due to the thermal shock. Whereas a long duration low temperature fire can result in a higher average temperature in the concrete members resulting in a greater reduction in concrete strength.

- The standard fires do not always represent the most severe fire conditions. Structural members having been designed to standard fires may fail to survive in real fires. For example, the modern offices tend to contain large quantities of hydrocarbon fuels in decoration, furniture, computers and electric devices, in forms of polymers, plastics, artificial leathers and laminates etc. Consequently, the fire becomes more severe than the conventional standard fire.

Although there are disadvantages and limitations of assuming the nominal fire curves and member design, the simplest and most common performance-based approaches have been developed based on the results and observations from standard fire resistance tests.

Considering, in a simplistic form, different fuel types and ventilation conditions, EN1991-1-2: 2002 and PD7974-1: 2003 provides the following nominal temperature-time curves:

| Code | Fire type | Application |
| --- | --- | --- |
| EN1991-1-2 | External Fire | For the outside of external walls which can be exposed to fire from different parts of the facade |
| EN1991-1-2 PD7974-1 | Standard Fire | Defined in EN1363-1 for representing a fully developed compartment fire |
| EN1991-1-2 PD7974-1 | Hydrocarbon | Representing a fire with hydrocarbon or liquid type fuel |
| PD7974-1 | Smouldering fire* | Representing slowly growing fire for products that are reactive under the influence of fire |
| * Note: This fire curve was developed so that materials such as intumescent coatings which rely upon chemical reactions could be subject to a test that addressed possible concerns regarding their intumescing behaviour. It was not meant to represent a design fire scenario (PD7974-3: 2003). |

EN1991-1-2 provides three nominal fire curves as follows:
a) For standard fire,

b) For external fire,

c) For hydrocarbon fire,

where

is the gas temperature in the fire compartment or near the member [°C];

t	is the time [min].

PD7974-1 adopts the same equations for the standard and hydrocarbon fires. However, the code provides alternative fire curve for large pool hydrocarbon fire, as well as a slow growing fire, as follows:
a) For large pool hydrocarbon fire,

b) For smouldering fire,

Figure 3 shows the various nominal fire curves for comparison. It can be seen that, over a period of 2 hours, the hydrocarbon fire is the most severe followed by the standard fire, with the external fire being the least severe fire although the slow heating fire represents the lowest temperature up to 30 minutes. It is noteworthy that for standard and smouldering fires, the temperature continuously increases with increasing time. For the external fire, the temperature remains constant at 680°C after approximate 22 minutes. Whereas for the hydrocarbon fires, the temperatures remain constant at 1100°C and 1120°C after approximate 40 minutes.

Figure 3 Nominal Fire curves

According to the nominal fire curves, the Eurocodes provide some heat transfer parameters for thermal analysis to structural members such as convection factor, emissivity of fire and surface emissivity of members. The structural response of the members in fire can be calculated. This ‘simple’ performance-based approach will generally allow more economical buildings to be designed and constructed compared to those designed using the prescriptive approach.

convection factor : Convective heat flux to the member related to the difference between the bulk temperature of gas bordering the relevant surface of the member and the temperature of that surface.

emissivity of fire: The amount of radiative heat the fire emits relative to the radiative heat emitted by a perfect black body at the same temperature

surface emissivity: The ratio between the radiative heat absorbed by a given surface and that of a black body surface. Equal to heat absorptive ability of a surface.

### Time Equivalence

The concept of time-equivalence is used to relate the severity of real fires to the time-temperature relationship in a standard fire test. Figure 4 illustrates the concept of time-equivalence, relating the actual maximum temperature of a structural member from an anticipated fire severity, to the time taken for the same member to attain the same temperature when subjected to the standard fire.

Figure 4: Concept of time-equivalence

There are a number of time-equivalence methods which take into account the amount of fuel load, compartment size, thermal characteristics of the compartment boundaries and ventilation conditions, including:

- Law (1971)

- Pettersson (1976)

- CIB W14 (1986)

- Harmathy (1987)

- BSEN1991-1-2 (2002)

Generally, time-equivalence can either be determined by using a simple equation or taken from experimental data from natural and standard fire tests. Although simple to use, the time-equivalence is a crude approximate method of modelling real fire behaviour and bears little relationship with real fire behaviour. In addition, the limitations of the method should be clearly understood. The main limitation is that the method is only applicable to the types of members used in the derivation of the adopted formulae.

In the following, the time-equivalence method given in EN1991-1-2 and the background research will be discussed.

### Time Equivalence - EN1991-1-2

The time-equivalence method present in Annex F (informative) of EN1991-1-2 is only valid for the members of:

- reinforced concrete

- protected steel

- unprotected steel

The equivalent time of exposure te, d [min] is given by:

where

kb	is a conversion factor related to the thermal inertia of the enclosure [min·m2/MJ];

kc	is a correction factor of the member material as given in Table 1[-];

qf, d	is the design fire load density [MJ/m2];

wf	is a ventilation factor as given in Eq. (7) [-].

Table 1 Correction factor kc for various materials according to EN1991-1-2

| Cross-section material | kc [-] |
| --- | --- |
| Reinforced concrete | 1.0 |
| Protected steel | 1.0 |
| Unprotected steel | 13.7xO* |

The conversion factor kb is related to the thermal inertia b of the enclosure as given in Table 2. It is noteworthy that the values assigned to kb in BSEN1991-1-2 may be replaced nationally by the values given PD7974-3 (2003) for use in UK, which have been validated by a test programme of natural fires in large compartments by British Steel (now Corus) and the Building Research Establishment (Kirby et al. 1994).

The calculations of the thermal inertia b for various compartment boundary conditions are given in Eqs  to  (Heating Phase in Parametric Fire Curves). Table 3 shows the values of thermal inertia b for some typical compartment lining materials. For compartments bounded with typical building surfaces, e.g. masonry and gypsum plaster, kb has a value of 0.07 according to PD7974-3. For compartments with high levels of insulation, e.g. proprietary wall insulation systems with mineral wools, kb has a value of 0.09.

The ventilation factor wf for a compartment with openings as shown in Figure 4 is given by:

with

αh = Ah / Af

αv = Av / Af				but 0.025 ≤ αv ≤ 0.25

bv = 12.5 (1 + 10αv - αv2 ≥ 10.0

where

Af	is the floor area of the compartment [m2];

Ah	is the area of horizontal openings in the roof [m2];

Av	is the area of vertical openings in the facade [m2];

H	is the height of the fire compartment [m].

For a small fire compartment, with a floor area Af < 100m2 and without openings in the roof, the ventilation factor wf can be calculated as:

where

O	is the opening factor as given in Eq.  (Heating Phase in Parametric Fire Curves).

At	is the total area of enclosure (walls, ceiling and floor, including openings) [m2].

Table 2 Values of conversion factor kb

| Thermal inertia b [J/m2s1/2K] | kb in EN1991-1-2 [min∙m2/MJ] | kb in PD7974-3 [min∙m2/MJ] |
| --- | --- | --- |
| > 2500 | 0.04 | 0.05 |
| 720 ≤ b ≤ 2500 | 0.055 | 0.07 |
| < 720 or No detailed assessment | 0.07 | 0.09 |

Table 3 Thermal inertia b for typical compartment lining materials (A.2 of PD7974-3)

| Boundary material | b [J/m2s1/2K] |
| --- | --- |
| Aerated concrete | 386 |
| Wool (pine) | 426 |
| Mineral wool | 426 |
| Vermiculit plaster | 650 |
| Gypsum plaster | 761 |
| Clay brick | 961 |
| Glass | 1312 |
| Fireclay brick | 1432 |
| Ordinary concrete | 1650 |
| Stone | 2423 |
| Steel | 12747 |

Figure 5: A fire compartment with horizontal and vertical openings

### Time Equivalence - Background Research

In 1993, British Steel (now Corus), in collaboration with the Building Research Establishment (BRE), carried out a test programme of nine natural fire simulations in large scale compartments to validate the time-equivalence method of Eurocode 1 (Kirby et al. 1994).

The tests were conducted in a compartment 23m long × 6m wide × 3m high constructed within the BRE ex-airship hanger testing facility at Cardington in Bedfordshire, UK. The test programme examined the effects of fire loads and ventilation on fire severity, and involved growing fires and simultaneous ignition, changes in lining material and compartment geometry.

The evaluation of the test results showed that the time-equivalence formula given in Eurocode 1 can be safely applied by using a value of conversion factor kb = 0.09 for compartments with realistic insulating materials. In fact, this value has been given in the CIB W14 report (1986). Consequently, it was recommended to adopt the values of kb = 0.07 and 0.05 for compartments with lower insulating performance. This recommendation has been adopted in the UK National Application Document (NAD) to ENV1991-2-2 (1996). It was argued that the values of (0.04, 0.055 and 0.07) given in ENV1991-2-2 as well as BSEN1991-1-2 (2002) might give unsafe assessments.

Table 4 summaries the comparison of the measured time-equivalences from the fire tests and the calculated values based on BSEN1991-1-2 with kb = 0.09 and 0.07 respectively. Obviously, the calculated time-equivalences based on kb = 0.09 are closer to the test results, with the ratios of test result to calculation varying from 0.71 to 1.11 and achieving a mean of 0.92. On the other hand, provided kb = 0.07, the ratios of test result to calculation fluctuate from 0.55 to 0.86 and give a mean of 0.72 which is too conservative.

Table 4 Comparison of test and calculated time-equivalences (Kirby et al. 1994)

Fuel controlled and ventilation controlled

The distinction between fuel controlled and ventilation controlled is critical to understanding compartment fire behavior. Compartment fires are generally fuel controlled while in the incipient and early growth stage and again as the fire decays and the demand for oxygen is reduced (see Figure 2).

While a fire is fuel controlled, the rate of heat release and speed of development is limited by fuel characteristics as air within the compartment and the existing ventilation profile provide sufficient oxygen for fire development. However, as the fire grows the demand for oxygen increases, and at some point (based on the vent profile) will exceed what is available. At this point the fire transitions to ventilation control. As illustrated in Figure 1, a ventilation controlled fire may reach flashover, all that is necessary is that sufficient oxygen be available for the fire to achieve a sufficient heat release rate for flashover to occur.

Fire Development with Limited Ventilation

### Parametric Fire Curves

The concept of parametric fires provides a rather simple design method to approximate post-flashover compartment fire. It is assumed that the temperature is uniform within the fire compartment. A parametric fire curve takes into account the compartment size, fuel load, ventilation conditions and the thermal properties of compartment walls and ceilings. Parametric fires will give more realistic estimates of the fire severity, for a given compartment, compared to the standard fires.

Annex A (informative) of EN1991-1-2 provides the most validated approach for determining parametric fires of compartments which will be described as follows.

- EN1991-1-2 Approach

- Other Parametric Models

- Background Research

### Parametric Fire Curves - EN1991-1-2

Figure 5 shows a typical parametric fire curve in accordance with EN1991-1-2. A complete fire curve comprises a heating phase represented by an exponential curve until a maximum temperature Θmax , followed by a linearly decreasing cooling phase until a residual temperature which is usually the ambient temperature. The fire intensity (Θmax) and fire duration (t*max) are two primary factors affecting the behaviour of a structure in fire. Consequently, they are adopted as the governing parameters in the design formulae for the parametric fires.

Figure 6: A typical parametric fire curve

Basically, the design formulae for parametric fire curves are simple to use with the aid of simple spreadsheets. However, attentions should be put on the limitations of the application as summarised below:

- maximum compartment floor area of 500m2;

- maximum compartment height of 4m;

- roof without openings;

- compartments with mainly cellulosic type fire loads;

- compartment linings with thermal inertia between 100 and 2200 J/m2s1/2K.

Note that these may change in the National Annex.

These limitations are established according to test data of the ‘Swedish’ fire curves and a database of more than 100 fire tests which have been used to calibrate the design formulae. The details can be found in BACKGROUND RESEARCH.

### Parametric Fire Curves - EN1991-1-2 - Heating Phase

In the heating phase, it is assumed that the gas temperature will rise with increase in time, which is independent on fire load. The parametric fire curve is given by:

where

Θg	is the gas temperature in the fire compartment [°C];

t*	is the parametric time to incorporate the ventilation conditions and compartment boundary conditions as given in Eq. (10) [hr].

The parametric time t* [hr] is given by:

with

where

b	is the thermal inertia of linings as given in Eq. (12) to [J/m2s1/2K];

O	is the opening factor as given in Eq. (11) [m1/2];

t	is the time [hr].

It is worth noting that when (= 1, Eq.(9) approximates the standard fire curve as shown in Figure 6.

Figure 7 Parametric fire curves with ( = 1

The opening factor O is given by:

but 0.02 ≤ O ≤ 0.20 [m1/2]

where

At	is the total area of enclosure (walls, ceiling and floor, including openings) [m2];

Av	is the total area of vertical openings on all walls [m2];

heq	height of vertical openings [m].

The thermal inertia b of an enclosure is determined by considering the combined effect of different thermal inertia in walls, ceiling and floor as follows:

where

Aj	is the area of enclosure surface j (walls, ceiling and floor), excluding openings [m2];

bj	is the thermal inertia of enclosure surface j (walls, ceiling and floor) as given in Eq.(12) and Figure 7) [J/m2s1/2K].

For an enclosure surface with single layer of material, its thermal inertia b is given by:

but 100 ≤ b ≤ 2200 [J/m2s1/2K]

where

c	is the specific heat capacity of boundary of enclosure at ambient temperature [J/kg L];

ρ	is the density of boundary of enclosure at ambient temperature [kg/m3];

λ	is the thermal conductivity of boundary of enclosure at ambient temperature [W/m K].

The values of thermal inertia b of some typical lining materials are given in Table 3 (Time Equvalence: EN1991-1-2 (2002) Approach).

For an enclosure surface with different layers of material, the thermal inertia b is determined according to Figure 7.

Figure 8 Enclosure surface with different layers of material

### Parametric Fire Curves - EN1991-1-2 - Heating Duration & Maximum Temperature

The duration of heating phase when t* = t*max, depending on the fire load density and the ventilation conditions, is given by:

with

but 50 ≤ qt,d ≤ 1000 [MJ/m2]

where

qf,d	is the fire load density related to the surface area Af of the floor [MJ/m2].

qt,d	is the fire load density related to the total surface area At of the enclosure [MJ/m2].

In case of tmax = tlim, the fire is fuel controlled. Otherwise, the fire is ventilation controlled. Figure 8 compares the heat release rates for fires with different fire growth rate. The categories of slow, medium, fast and ultra-fast fire growth rates basically depend on the types of occupancy.

Figure 9 Fire growth rate and rate of heat release for different occupancies

However, there are further limits on the maximum time tmax. The Code states that when tmax = tlim, the parametric t* in the main equation is replaced by:

with

where tlim is given in Eq. (10).

In case of (O > 0.04 and qt,d < 75 and b < 1160), (lim in Eq. (10) has to be multiplied by factor k given by:

### Parametric Fire Curves - EN1991-1-2 - Cooling Phase

EN1991-1-2 defines linear temperature-time curves for the cooling phase after the heating phase of parametric fire curves. Depending on the value of tmax* , three different linear curves for gas temperature Θg are defined as follows:

with

### Parametric Fire Curves -Other Parametric Models

The concepts of post-flashover compartment fires and the predictions of their temperatures have long been studied by many researchers. Thus, a wide variety of parametric fire models exist. The majority of the models have been developed by curve-fitting against either model predictions or fire test results. This section will review some of the models.

- Lie's Model (1974)

- Ma & Mäkeläinen's Model

### Parametric Fire Curves -Other Parametric Models - Lie's Model (1974)

Lie (1974) proposed a model comprising a nonlinear heating phase up to the maximum temperature reached during the fire, followed by a linear cooling phase. The parametric fire curve in the heating phase was given by:

where

Θg	is the gas temperature in the fire compartment [°C];

C	=0 for heavy weight compartment boundary materials with density ρ ≥ 166 kg/m3;

=1 for lightweight materials with ρ < 1600 kg/m3;

O	is the opening factor [m1/2];

t	≤ (4.8O+60) is the time [min].

The duration of heating phase t*max [min] was given by:

where qt,d is the fire load density related to the total surface area At of the enclosure [MJ/m2].

In the cooling phase, gas temperature Θg was given by:

where

Θmax 	is the maximum gas temperature reached at t*max [°C].

### Parametric Fire Curves -Other Parametric Models - Mäkeläinen's Model (2000)

Ma & Mäkeläinen (2000) proposed a parametric fire curve for small and medium compartment fires. In their study, a total of 25 complete gas temperature-time curves from different laboratories around the world had been considered. The main parameters of the fire curves include:

- Floor area:	< 100	m2

- Compartment height:	≤ 4.5	m

- Fire load density	10-40	kg/m2

- Ventilation factor:	5-16	m5/2

- Boundary thermal inertia:	555-1800	J/m2s1/2K

These fire curves were first non-dimensionalised by the maximum gas temperature and the time to reach the maximum temperature, as shown in Figure 10. It can be seen that these fire curves display similar shape. By curve-fitting against the test data, the authors derived a non-dimensional expression as follows:

where

Tg	is the gas temperature [°C];

Tgm	is the maximum gas temperature [°C];

T0	is the room temperature [°C];

t	is the time [min];

tm	is the time corresponding to the maximum gas temperature [min];

δ	is the shape constant of the curve, which has different values for the heating and cooling phases. The value for the heating phase is twice that for the cooling phase.

The authors reported that the shape constants δ = (0.8, 1.6) had the best fit with the test data, whereas δ = (0.5, 1.0) formed the upper envelope, as shown in Figure 9.

Figure 10 Non-dimensionalized fire curves (Source: Ma & Mäkeläinen (2000))

The maximum temperature Tgm [°C] was given by:

with

where

At	is the total surface area of compartment boundaries (openings included) [m2];

Aw	is the area of openings [m2];

h	is the height of the openings [m];

η	is the inverse of opening factor [m-½;];

ηcr	is the inverse of the opening factor in the critical region [m-½;];

φ	is the surface area ratio of fuel [m2/kg];

κ	is the ratio of floor area Af to the total surface area At in a fire compartment [-];

q	is the fire load density per unit floor area [kg of wood/m2];

Tgmcr	is the maximum temperature in the critical region, which can be obtained by substituting Ηcr into Eq.(22) [°C].

Assuming a constant burning rate R during the entire period of primary burning, the fire duration τ was given by:

with

where

D	is the depth of the fire compartment [m];

G0	is the total fire load of equivalent woods [kg];

R	is the burning rate [kg of wood/min]

W	is the width of the wall which contains opening [m].

The time to reach the maximum temperature tm was approximated by:

### Parametric Fire Curves -Background Research - Wickström's Model

The background theory of the parametric fire model of BSEN1991-1-2 was developed by Wickström (1981/82). Based on the heat balance for a fire compartment as shown in Figure 1, he suggested that the compartment fire depended entirely on the ratio of the opening factor to the thermal inertia of the compartment boundary. He used the test data of the ‘Swedish’ fire curves (Magnusson & Thelandersson 1970) to validate his theoretical assumptions. Figure 2 shows a set of Swedish fire curves for different fuel loads with an opening factor of 0.04 m½. By curve-fitting, Wickström expressed the compartment fire in a single power formula for the heating phase, in which the standard fire curve could be attained by assigning a ventilation factor of 0.04 m½ and a thermal inertia of 1165 J/m2 s½ K.

Figure 1 Heat balance of a fire compartment


Figure 2 Temperature-time curves for different fuel loads (MJ/m2 of total surface area) (Source: Drysdale 1999)

The cooling phase of a natural fire is a complex process due to the depletion of the fuel or the active intervention of the fire fighting activities or sprinkler systems. The fire duration depends on the combustion rate which is related to the fuel type, fuel distribution and ventilation conditions. For the sake of simplicity, Wickström defined linear temperature-time curves for the cooling phase of the fire.

Due to the experimental characteristics of the ‘Swedish’ fire curves, the original application of Wickström’s parametric fire curves had extensive limitations. For example, in the pre-standard ENV1991-2-2, it stated that the design equations were only valid for compartments with floor areas up to 100 m2. The compartment linings were also restricted to thermal inertia between 1000 and 2200 J/m2s½K, which meant the highly insulated materials could not be taken into account.

### Parametric Fire Curves -Background Research - ECSC Research Project

The validity of the background theory, as well as the application assumptions and limitations, for the parametric fire curves of Eurocode 1, the ENV1991-2-2:1996 version, have been investigated in an extensive research programme “Natural Fire Safety Concept” supported by the European Coal and Steel Community (ECSC) in between 1994 and 1998. It has been undertaken by 11 European partners. A database of more than 100 natural fire tests made in Australia, France, the Netherlands and UK in between 1973 and 1997 had been compiled (Schleich & Cajot 1999). In 1999 and 2000, more full-scale large compartment fires were carried out by Building Research Establishment (BRE) at Cardington in UK to further supplement the database (Lennon & Moore 2003).

The first phase of the programme included one study focusing on the theoretical developments (Cadorin 2003), leading to the improvements in BSEN1991-1-2 on the following aspects:

- the method for incorporating enclosure surfaces with different layers of material

- the consideration of fuel controlled fires

- some modifications in the cooling phase

A total of 48 experimental tests from the database had been used in the comparison study. The BRE tests in 1999 and 2000 were not included because the tests were performed after this study. The main characteristics of these tests are listed in Table 5.

Table 5 Main parameters of natural fire tests for verifying parametric fire curves of Eurocode 1

Figure 1 shows the plots of the test maximum temperature versus the predictions for each test by using the design models of ENV1991-2-2 and BSEN1991-1-2. For the tests, the maximum temperatures were the average value of several measurements made by different thermocouples located in the compartments. The regression analysis showed that there was a poor correlation between the test results and the predictions by ENV1991-2-2, with the coefficient of correlation of 0.19 only. Relatively, the improvements proposed for BSEN1991-1-2 led to a much better correlation between the model and the test results.

Figure 1 Comparison of maximum temperatures from test results and predictions by Eurocode 1 (Source: Schleich & Cajot 1999)

The second phase of the ESCS research programme was to provide high-quality test data on the behaviour of post-flashover fires in realistic compartments for validating the design approach. A series of eight full-scale fire tests in a 12×12m compartment was carried out by BRE at Cardington in the UK in 1999 and 2000 (Lennon & Moore 2003). The main characteristics of these tests are given in Table 5.

The findings of the tests lead to a number of significant changes in BSEN1991-1-2, including:

- the scope of application of the design method

- the method of determining the effect of compartment boundaries

- the calculation of time to maximum temperature

### Localised Fires

A compartment fire should be taken as localised or pre-flashover fire when flashover is unlikely to occur. Depending on the size of the fire and the compartment, a localised fire may or may not impinge on the ceiling of the compartment. The temperature in the fire flame and plume and the surrounding gas are not uniform, and need to be determined separately. This is the main difference from a post-flashover fire where the temperature assumed to be uniform within the fire compartment.

Annex C (informative) of BSEN1991-1-2 provides a simple calculation approach for determining localised fires of compartments which will be described as follows.

- EN1991-1-2 (2002) Approach

- Background Research - Ceiling Jet Temperature

### Localised Fires - EN1991-1-2 (2002) Approach

EN1991-1-2 provides the simple approach for determining the thermal action of localised fires in Annex C (informative). Depending on the height of the fire flame relative to the ceiling of the compartment, a localised fire can be defined as either a small fire or a big flame. For a small fire, a design formula has been given to calculate the temperature in the plume at heights along the vertical flame axis. For a big fire, some simple steps have been developed to give the heat flux received by the fire exposed surfaces at the level of the ceiling.

The limitations of the approach include:

- The diameter of fire D ≤ 10 m

- The rate of heat release or the fire Q ≤ 50 MW

However, the approach can be applied to the cases of several localised fires.

- Smaller Fires or Open-Air Fires

- Larger Fires Impacting Ceiling

- Multiple Fires

### Localised Fires - EN1991-1-2 - Small Fires

In a localised fire as shown in Figure 1, the highest temperature is at the vertical flame axis (or plume centreline), decreasing toward the edge of the plume. The flame axis temperature Θ(z) changes with height. It is roughly constant in the continuous flame region and represents the mean flame temperature. The temperature decreases sharply above the flames as an increasing amount of ambient air is entrained into the plume (Karlsson & Quintiere 1999).

EN1991-1-2 provides a design formula to calculate the temperature in the plume of a small localised fire, based on the fire flume model developed by Heskestad (1995). It can be applied to open-air fires as well.

Considering a localised fire as shown in Figure 1, the flame height Lf of the fire is given by:

where

D	is the diameter of the fire [m];

Q	is the rate of heat release of the fire [W].

H	is the distance between the fire source and the ceiling [m];

In case of fire do not impinge on the ceiling of the compartment when Lf < H, or fire in open fire, the temperature Θ(z) in the plume along the symmetric vertical flame axis is given by:

with

where

Qc	is the convective part of the rate of heat release [W], with Qc = 0.8 Q by default;

z	is the height along the flame axis [m];

z0	is the virtual origin of the axis [m].

The virtual origin z0 depends on the diameter of the fire D and the rate of heat release Q. This empirical equation has been derived from experimental data. The value of z0 may be negative and locate beneath the fuel source, indicating that the area of the fuel source is large compared to the energy being released over that area (see Figure 1). For fire sources where the fuel releases high energy over a small area, z0 may be positive and locate above the fuel source.

Figure 1 Schematic diagram for small localised fires

### Localised Fires - BSEN1991-1-2 - Larger Fires Impacting Ceiling

When a localised fire becomes large enough with Lf ≥ H, the fire flame will impinge on the ceiling of the compartment. The ceiling surface will cause the flame to turn and move horizontally beneath the ceiling. Figure 1 shows a schematic diagram of a localised fire impacting on the ceiling with the ceiling jet flowing beneath an unconfined ceiling. As the ceiling jet moves radially outward, it loses heat to the cooler ambient air being entrained into the flow, as well as the heat transfer to the ceiling. Generally, the maximum temperature occurs relatively close to the ceiling (Karlsson & Quintiere 1999).

Figure 1 Localised fires impacting on ceiling of compartment

EN1991-1-2 only provides design formulae to determine the heat flux received by the surface area at the ceiling level, but not for calculating the ceiling jet temperatures. The simple approaches for determining the ceiling jet temperatures will be briefly discussed in Background Research – Ceiling Jet Temperatures.

Considering a localised fire impacting the ceiling of the compartment as shown in Figure 1 (Lf ≥ H), the horizontal flame length Lh is given by:

with

where

Lh	is the horizontal flame length as given by Eq.(1) [m];

H	is the distance between the fire source and the ceiling [m];

QH*	is a non-dimensional rate of heat release [-];

Q	is the rate of heat release of the fire [W].

The heat flux  [W/m2] received by the fire exposed unit surface area at the ceiling level at the distance r from the flame axis is given by:

with

where

r	is the horizontal distance from the vertical flame axis to the point along the ceiling where the thermal flux is calculated [m];

z'	is the vertical position of the virtual heat source as given by Eq.(3) [m];

D	is the diameter of the fire [m];

The vertical position of the virtual heat source z' is given by:

with

The net heat flux received by the fire exposed unit surface at the level of the ceiling is given by:

where

αc	is the coefficient of heat transfer by convection as given in Table [W/m2K];

εf	is the emissivity of the fire;

εm	is the surface emissivity of the member;

Φ	is the configuration factor;

Θm	is the surface temperature of the member [°C].

σ	is the Stephan Boltzmann constant (= 5.67×10-8 W/m2K4);

is the heat flux received by the fire exposed unit surface area at the level of the ceiling as given by Eq.(2).

### Localised Fires - EN1991-1-2 - Multiple Fires

In the case of several localised fires, the individual heat fluxes  received by the fire exposed unit surface area at the ceiling level should be first calculated. The total heat flux [W/m2] is then taken as the summation of the contribution of all localised fires as follows:

### Localised Fires - Background Research - Ceiling Jet Temperatures

Alpert (1972) has developed empirical equations for determining the maximum temperature and velocity in a ceiling jet flow produced by a steady fire. The empirical equations are based on experimental data collected for fuels such as wood and plastic pallets, cardboard boxes, plastic products in cardboard boxes, and liquids with heat release rates ranging from 668 kW to 98 MW under ceiling heights from 4.6 to 15.5 m (Evans 1995). The maximum temperature T [°C] of a ceiling jet as shown in Figure is given by:

see notation for equations below.

Heskestad and Delichatsios (1978) have developed different empirical equations for maximum ceiling jet temperature rises and velocities, based on testing subsequent to Alpert’s study (Evans 1995). The temperature rise ΔT of a ceiling jet is given by:

with

see notation for equations below.

Notation for equations

H	is the ceiling height [m];

Q	is the rate of heat release of the fire [kW];

r	is the radial position from the flame axis [m];

T∞	is the ambient gas temperature [=293K];

ρ∞	is the ambient gas density [=1.2 kg/m3];

cp	is the heat capacity at constant pressure [kJ/kg K];

g	is the gravitational acceleration [=9.81 m/s2]

Beyler (1986) has conducted a comprehensive review on the empirical models for ceiling jet temperature rise and velocity.